Oceanside Fire Requirements

TO:
Development Services/Engineering  
FROM:
Anne Marie Bland

Plans Examiner

DATE:
November 18, 2019
SUBJECT:
Improvement plan R19-00013

Melrose Heights


Melrose & Oceanside


PA 1
Fire Prevention comments on Grading/Improvement Plans
The following items will need to be addressed in order to deem the plan complete.

Fire Prevention Requirements: 
1. Show location of fire sprinkler connections (DCDA) and fire department connections for all buildings with NPFA 13R and 13 fire sprinkler systems.

2. Private underground fire line size subject to fire sprinkler system hydraulic calculations.  Add this note to the plans.
3. Private underground fire lines shall not be installed based on civil or grading plans. Separate Fire Department plan review submittal required for private underground fire lines. Private underground fire lines must be inspected by the Fire Department.  Add this note to the plans.
4. Prior to the delivery of combustible building materials and the start of combustible construction, paved fire access roadways must be installed so that all portions of exterior walls of buildings under construction are within 150 unobstructed feet to a fire access roadway.
5. On-site fire hydrants within 400 unobstructed feet of all portions of exterior walls of buildings under construction must be installed, tested, and serviceable prior to delivery of combustible building materials and the start of combustible construction.

6. Pre-construction meeting must be scheduled with the fire department to verify items 1 and 2 have been completed.  Pre-construction meeting is required prior to delivery of combustible material and start of combustible construction.

