Oceanside Fire Requirements

TO:	Landscape Plans

FROM:	Tim Rise

Plans Examiner

DATE:	February 9, 2024

SUBJECT:	Landscape plans

South River Village

L23-00050 (ADM22-00064)

Fire Prevention comments on Landscape Plans

The following items will need to be addressed in order to deem the plan complete.

- A clearance of three feet in all directions shall be maintained around all fire hydrants and DCDA. A path to the appliance is also required for access.

- Proposed vegetation around the fire protection appliances all have a maturity growth over 3’ in height. These appliances need to be visible at all times. Lower growth vegetation is required.