Oceanside Fire Requirements

TO:
Development Services/Engineering  
FROM:
Anne Marie Bland

Plans Examiner

DATE:
November 14, 2017
SUBJECT:
Grading Plan R17-00019

Vista Pacific


2300 Rancho del Oro Road
Fire Prevention comments on Grading/Improvement Plans
The following items will need to be addressed in order to deem the plan complete.

Fire Prevention Requirements: 
1. Provide approved cul-de-sac turn around at the end of the private street.

2. Private street must be marked no parking per Oceanside Fire standard.

3. Prior to the delivery of combustible building materials and the start of combustible construction, paved fire access roadways must be installed so that all portions of exterior walls of buildings under construction are within 150 unobstructed feet to a fire access roadway.
4. On-site fire hydrants must be installed, tested, and serviceable prior to delivery of combustible building materials and the start of combustible construction.
5. Pre-construction meeting must be scheduled with the fire department to verify items 1 and 2 have been completed.  Pre-construction meeting is required prior to delivery of combustible material and start of combustible construction.

